## Cover
Electrical Design Calculations: G+2 Commercial Office Building
Prepared by Anuj Kumar (B.Tech EE, DTU). Portfolio design exercise
Sheet | What it contains
Inputs | Design inputs and assumptions: supply, margins, loading limits, derating, soil data. Change these and every sheet updates.
Lighting | Lumen-method lighting design per space (room index, UF, MF, fixture count, achieved lux, LPD vs ECBC 2017).
Load_Schedule | Connected load, demand factors, maximum demand (kW/kVAr/kVA), essential (DG) and UPS-backed loads, feeder tagging.
Sizing | Transformer, DG, UPS + battery and APFC sizing; LV full-load current and fault level.
Cable_Schedule | Feeder cables from the Main LT Panel: breaker rating, derating, size by ampacity and by voltage drop, final selection.
Earthing | Earth electrode resistance (IS 3043), number of electrodes, strip interconnection, earth conductor sizing.
Ref_Tables | Cable data, utilisation factors, standard equipment ratings, IS 3043 parallel-electrode factors.
Colour legend
Blue text, yellow fill | Input: edit these
Black text | Formula: do not overwrite
Green text | Link from another sheet
Green fill | Key result / selected equipment
Building basis
Ground + 2 floors, 600 m² per floor (30 m x 20 m), commercial office, Delhi.
GF: reception/lobby, cafeteria, open office, electrical room. FF & SF: open office, cabins, meeting room.
Supply: 11 kV HT from DISCOM → 11/0.433 kV Dyn11 oil-type transformer → Main LT Panel (MLTP). DG backup via AMF panel; UPS for IT loads; APFC at MLTP.
Earthing system: TN-S at LV.
Codes & standards referred
IS 732:2019 (wiring installations); IS 3043:2018 (earthing); IS 3646 / NBC 2016 Part 8 Sec 2 (lighting & electrical); ECBC 2017 (lighting power density)
IS 1180 (distribution transformers); IEC 60502-1 / IS 7098 (XLPE cables); IEC 60364-5-52 (cable selection, voltage drop); CEA (Measures relating to Safety & Electric Supply) Regulations 2023
Limitations
Cable data from the Havells International Cables catalogue (IEC 60502-1). Reactance is a typical value since the catalogue does not list it.
Demand factors are typical consultant practice. Confirm them against the client brief and DISCOM requirements.
Short-circuit withstand of cables and the DG transient response (ISO 8528-5) still need checking with manufacturer data.

## Inputs
Design inputs
Parameter | Value | Unit | Basis / note
Area per floor | 600 | m² | 30 m x 20 m
Number of floors | 3 | nos | G + 2
HT supply voltage | 11 | kV | DISCOM 11 kV supply (load above LT limit, so confirm with DISCOM)
LT system voltage (L-L) | 415 | V | 3-ph, 4-wire, 50 Hz
Overall diversity factor | 0.9 | - | Applied over the sum of feeder demands
Future expansion margin | 20% | - | 20%: typical consultant allowance
Transformer max loading | 0.8 | - | Sized for ≤80% loading at full demand + margin
Transformer impedance | 0.045 | p.u. | IS 1180 typical for 250–630 kVA
DG max loading | 0.8 | - | Prime-rated DG at ≤80%
Target power factor | 0.98 | - | DISCOM incentive range
UPS output PF | 0.9 | - | Online double-conversion UPS
UPS efficiency | 0.93 | -
UPS battery backup time | 0.5 | h | 30 min
Battery DC bus voltage | 384 | V | 32 x 12 V VRLA blocks
Battery ageing / design factor | 1.25 | - | IEEE 485 ageing factor
UPS battery charging allowance | 10% | - | Added to UPS input demand
Feeder voltage-drop limit | 3% | - | 3% on main feeders; ≤5% end-to-end (IS 732 / IEC 60364-5-52)
Temperature derating factor | 0.87 | - | Havells rating factor for 45°C air (catalogue base 30°C)
Grouping derating factor | 0.71 | - | Havells: multicore touching, 2 racks x 4 cables
Soil resistivity ρ | 50 | Ω·m | Assumed for Delhi alluvium; lies within the 10–130 Ω·m range reported for West Delhi (2014 resistivity survey). Replace with site Wenner 4-point test (IS 3043)
Earth electrode length L | 3 | m | GI pipe electrode
Effective electrode diameter d | 0.1 | m | 40 mm pipe in 100 mm bore with backfill compound
Electrode spacing s | 6 | m | ≥ 2L
Target earth grid resistance | 1 | Ω | Typical requirement for substation earth grid
Interconnecting strip length | 60 | m | Buried ring/link strip between pits
Strip width w | 0.05 | m | 50 mm
Strip burial depth t | 0.5 | m
Earth fault clearing time | 1 | s | Conservative (IS 3043)
k factor, GI steel | 80 | - | IS 3043, bare steel
Corrosion allowance on earth conductor | 1.5 | - | Multiplier on minimum area

## Lighting
Lighting design: lumen method N = (E x A) / (Φ x UF x MF)
Hm = luminaire to working plane (3.0 m false ceiling − 0.75 m desk = 2.25 m). Room index K = A / (Hm x (L + W)). UF from Ref_Tables.
Floor | Space | Length (m) | Width (m) | Area (m²) | Hm (m) | Room index K | UF | MF | Target lux (E) | Luminaire | Lumens / fixture | W / fixture | Fixtures (N) | Achieved lux | Installed W | LPD (W/m²) | ECBC limit (W/m²) | Check
GF | Reception / lobby | 10 | 10 | 100 | 2.25 | 2.2222 | 0.72 | 0.8 | 150 | LED downlight 18 W | 1800 | 18 | 15 | 155.52 | 270 | 2.7 | 9.5 | OK
GF | Cafeteria | 15 | 10 | 150 | 2.25 | 2.6667 | 0.75 | 0.8 | 200 | LED downlight 18 W | 1800 | 18 | 28 | 201.6 | 504 | 3.36 | 9.5 | OK
GF | Open office | 20 | 15 | 300 | 2.25 | 3.8095 | 0.78 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 41 | 307.008 | 1476 | 4.92 | 9.5 | OK
GF | Electrical room | 10 | 5 | 50 | 2.25 | 1.4815 | 0.63 | 0.8 | 150 | LED batten 20 W | 2000 | 20 | 8 | 161.28 | 160 | 3.2 | 9.5 | OK
FF | Open office | 25 | 18 | 450 | 2.25 | 4.6512 | 0.81 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 58 | 300.672 | 2088 | 4.64 | 9.5 | OK
FF | Cabins | 10 | 8 | 80 | 2.25 | 1.9753 | 0.67 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 13 | 313.56 | 468 | 5.85 | 9.5 | OK
FF | Meeting room | 10 | 7 | 70 | 2.25 | 1.8301 | 0.67 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 11 | 303.2229 | 396 | 5.6571 | 9.5 | OK
SF | Open office | 25 | 18 | 450 | 2.25 | 4.6512 | 0.81 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 58 | 300.672 | 2088 | 4.64 | 9.5 | OK
SF | Cabins | 10 | 8 | 80 | 2.25 | 1.9753 | 0.67 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 13 | 313.56 | 468 | 5.85 | 9.5 | OK
SF | Meeting room | 10 | 7 | 70 | 2.25 | 1.8301 | 0.67 | 0.8 | 300 | LED panel 600x600 36 W | 3600 | 36 | 11 | 303.2229 | 396 | 5.6571 | 9.5 | OK
| Total |  |  | 1800 | [8 empty] | 256 |  | 8314 | 4.6189
Lux targets per NBC 2016 Part 8 / IS 3646 (office 300, cafeteria 200, lobby & plant room 150). MF 0.8 for LED in clean office. ECBC 2017 building-area LPD (office) 9.5 W/m². Corridors and toilets not included.

## Load_Schedule
Load schedule & maximum demand
MD = Connected load x Demand factor. kVAr = kW x tan(cos⁻¹ PF). DG demand uses its own factor (load shedding on DG). Feeder tag links each load to its MLTP outgoing feeder (Cable_Schedule).
S.No | Floor / area | Load | Feeder | Qty | kW / unit | Connected load (kW) | PF | Demand factor | MD (kW) | MD (kVAr) | MD (kVA) | Essential (DG) | DG factor | DG demand (kW) | DG demand (kVAr) | UPS backed | Notes
1 | GF | Lighting (LED) | F01 | 1 | 2.41 | 2.41 | 0.9 | 0.9 | 2.169 | 1.0505 | 2.41 | Y | 0.9 | 2.169 | 1.0505 | N | From Lighting sheet
2 | GF | 6A raw power sockets | F01 | 40 | 0.1 | 4 | 0.8 | 0.3 | 1.2 | 0.9 | 1.5 | Y | 0.3 | 1.2 | 0.9 | N
3 | GF | 16A power sockets | F01 | 8 | 1 | 8 | 0.8 | 0.4 | 3.2 | 2.4 | 4 | Y | 0.4 | 3.2 | 2.4 | N
4 | GF | Cafeteria / pantry equipment | F01 | 1 | 15 | 15 | 0.9 | 0.6 | 9 | 4.3589 | 10 | Y | 0.6 | 9 | 4.3589 | N
5 | GF | Toilet exhaust fans | F01 | 4 | 0.1 | 0.4 | 0.8 | 1 | 0.4 | 0.3 | 0.5 | Y | 1 | 0.4 | 0.3 | N
6 | GF | Server room split AC | F01 | 1 | 2.5 | 2.5 | 0.85 | 1 | 2.5 | 1.5494 | 2.9412 | Y | 1 | 2.5 | 1.5494 | N
7 | GF | Workstation UPS sockets | F08 | 25 | 0.15 | 3.75 | 0.9 | 0.8 | 3 | 1.453 | 3.3333 | Y | 0.8 | 3 | 1.453 | Y | Fed via UPS
8 | GF | Server / IT rack | F08 | 1 | 5 | 5 | 0.9 | 1 | 5 | 2.4216 | 5.5556 | Y | 1 | 5 | 2.4216 | Y | Fed via UPS
9 | FF | Lighting (LED) | F02 | 1 | 2.952 | 2.952 | 0.9 | 0.9 | 2.6568 | 1.2867 | 2.952 | Y | 0.9 | 2.6568 | 1.2867 | N | From Lighting sheet
10 | FF | 6A raw power sockets | F02 | 60 | 0.1 | 6 | 0.8 | 0.3 | 1.8 | 1.35 | 2.25 | Y | 0.3 | 1.8 | 1.35 | N
11 | FF | 16A power sockets | F02 | 10 | 1 | 10 | 0.8 | 0.4 | 4 | 3 | 5 | Y | 0.4 | 4 | 3 | N
12 | FF | Toilet exhaust fans | F02 | 4 | 0.1 | 0.4 | 0.8 | 1 | 0.4 | 0.3 | 0.5 | Y | 1 | 0.4 | 0.3 | N
13 | FF | Workstation UPS sockets | F08 | 60 | 0.15 | 9 | 0.9 | 0.8 | 7.2 | 3.4871 | 8 | Y | 0.8 | 7.2 | 3.4871 | Y | Fed via UPS
14 | SF | Lighting (LED) | F03 | 1 | 2.952 | 2.952 | 0.9 | 0.9 | 2.6568 | 1.2867 | 2.952 | Y | 0.9 | 2.6568 | 1.2867 | N | From Lighting sheet
15 | SF | 6A raw power sockets | F03 | 60 | 0.1 | 6 | 0.8 | 0.3 | 1.8 | 1.35 | 2.25 | Y | 0.3 | 1.8 | 1.35 | N
16 | SF | 16A power sockets | F03 | 10 | 1 | 10 | 0.8 | 0.4 | 4 | 3 | 5 | Y | 0.4 | 4 | 3 | N
17 | SF | Toilet exhaust fans | F03 | 4 | 0.1 | 0.4 | 0.8 | 1 | 0.4 | 0.3 | 0.5 | Y | 1 | 0.4 | 0.3 | N
18 | SF | Workstation UPS sockets | F08 | 60 | 0.15 | 9 | 0.9 | 0.8 | 7.2 | 3.4871 | 8 | Y | 0.8 | 7.2 | 3.4871 | Y | Fed via UPS
19 | Terrace | VRF outdoor units (~30 TR per floor) | F04 | 9 | 10 | 90 | 0.9 | 0.85 | 76.5 | 37.0506 | 85 | Y | 0.5 | 45 | 21.7945 | N | 50% HVAC on DG (load shedding)
20 | All floors | VRF indoor units / FCU fans | F04 | 30 | 0.1 | 3 | 0.85 | 0.9 | 2.7 | 1.6733 | 3.1765 | Y | 0.9 | 2.7 | 1.6733 | N
21 | Terrace | Fresh-air / ventilation fans | F04 | 3 | 1.5 | 4.5 | 0.85 | 1 | 4.5 | 2.7888 | 5.2941 | Y | 1 | 4.5 | 2.7888 | N
22 | Lift core | Passenger lift, 8-pax, VVVF | F05 | 1 | 11 | 11 | 0.85 | 1 | 11 | 6.8172 | 12.9412 | Y | 1 | 11 | 6.8172 | N
23 | Pump room | Domestic transfer pumps (1W + 1S) | F06 | 2 | 3.7 | 7.4 | 0.85 | 0.5 | 3.7 | 2.2931 | 4.3529 | Y | 0.5 | 3.7 | 2.2931 | N | Standby not simultaneous
24 | Pump room | Sewage treatment plant | F06 | 1 | 5.5 | 5.5 | 0.85 | 0.8 | 4.4 | 2.7269 | 5.1765 | Y | 0.8 | 4.4 | 2.7269 | N
25 | Pump room | Main fire pump (electric) | F07 | 1 | 30 | 30 | 0.85 | 0 | 0 | 0 | 0 | Y | 1 | 30 | 18.5923 | N | Runs only during fire; HVAC shed then. Full on DG
26 | Pump room | Jockey pump | F07 | 1 | 3.7 | 3.7 | 0.85 | 0.2 | 0.74 | 0.45861 | 0.87059 | Y | 1 | 3.7 | 2.2931 | N | Intermittent
27 | Parking | EV chargers, AC 7.4 kW | F09 | 2 | 7.4 | 14.8 | 0.99 | 1 | 14.8 | 2.1089 | 14.9495 | N | 0 | 0 | 0 | N | Not on DG
28 | External | Landscape / street lighting | F10 | 1 | 3 | 3 | 0.9 | 1 | 3 | 1.453 | 3.3333 | Y | 1 | 3 | 1.453 | N
29 | External | Signage | F10 | 1 | 1 | 1 | 0.9 | 1 | 1 | 0.48432 | 1.1111 | Y | 1 | 1 | 0.48432 | N
|  | TOTAL (before diversity) |  |  |  | 271.664 |  |  | 180.9226 | 91.1358 | 202.5801 |  |  | 167.5826 | 94.1975

## Sizing
Equipment sizing: transformer, DG, UPS, APFC
A. Maximum demand
Item | Value | Unit | Formula / note
Total connected load | 271.664 | kW | Load_Schedule total
Sum of feeder MD | 180.9226 | kW | Σ (CL x DF)
Sum of feeder MD (reactive) | 91.1358 | kVAr
Building MD after diversity | 162.8303 | kW | x overall diversity factor
Building MD after diversity (reactive) | 82.0222 | kVAr
Building MD | 182.3221 | kVA | √(kW² + kVAr²)
Uncorrected power factor | 0.89309 | -
B. Distribution transformer (11/0.433 kV, Dyn11, ONAN)
Item | Value | Unit | Formula / note
Required rating | 273.4832 | kVA | MD x (1 + margin) / max loading
Selected transformer | 315 | kVA | Next IS 1180 standard rating
Loading at present MD | 57.88% | -
LV full-load current | 438.2297 | A | kVA x 1000 / (√3 x V)
HV full-load current | 16.5332 | A
LV fault level (infinite source) | 9.7384 | kA | I_FL / Z%. Conservative; MLTP rated 25 kA, 1 s
C. Diesel generator (AMF, prime rated)
Item | Value | Unit | Formula / note
Essential demand | 150.8243 | kW | Σ DG demand x diversity
Essential demand (reactive) | 84.7778 | kVAr
Essential demand | 173.0181 | kVA
Required rating | 259.5271 | kVA | x (1 + margin) / max loading
Selected DG set | 320 | kVA | Next standard rating, 415 V, 0.8 PF
Loading at essential demand | 54.07% | -
Fire pump starting kVA (star-delta) | 78.4314 | kVA | kW / (η x PF) x LRC 6 / 3 for star-delta. Largest motor step
Starting kVA as % of DG rating | 24.51% | - | Confirm voltage dip with DG maker (ISO 8528-5)
DG full-load current | 445.1857 | A
D. UPS & battery (online, double conversion)
Item | Value | Unit | Formula / note
UPS-backed demand | 22.4 | kW | Σ MD where UPS backed = Y
UPS-backed demand | 24.8889 | kVA | kW / UPS output PF
Required rating | 29.8667 | kVA | x (1 + margin)
Selected UPS | 30 | kVA | Next standard rating
UPS loading | 82.96% | -
Battery capacity required | 47.253 | Ah | P_rated x t x ageing / (V_dc x η). Check against maker's constant-power tables
Selected battery | 65 | Ah | 32 x 12 V VRLA blocks
UPS input demand | 33.6163 | kVA | Rated kW / η x (1 + charging), at 0.95 input PF. Used for UPS feeder
E. APFC panel
Item | Value | Unit | Formula / note
Required compensation | 48.9581 | kVAr | P x (tan φ1 − tan φ2)
Selected APFC panel | 75 | kVAr | x (1 + margin), in 25 kVAr steps; 7% detuned reactors (VRF/UPS harmonics)

## Cable_Schedule
LT cable schedule: Main LT Panel feeders
Breaker In ≥ Ib; cable Iz (derated) ≥ In; ΔV% = mV/A/m x I x L / (1000 x V) ≤ limit. Size = larger of ampacity and voltage-drop requirement. 0.6/1 kV Al XLPE armoured (Havells), 3.5 core (4 core for 16 mm²), on tray.
Tag | From | To | Load basis | Load (kVA) | Ib (A) | Breaker In (A) | Length (m) | Runs | Temp factor | Group factor | Total derating | Iz needed / run (A) | Idx (ampacity) | Max mV/A/m for ΔV | Idx (ΔV) | Final idx | Size (mm²) | Cable | Iz derated total (A) | ΔV (%) | Check | Governed by
I01 | Transformer | Main LT Panel | Transformer rating | 315 | 438.2297 | 500 | 15 | 2 | 0.87 | 0.71 | 0.6177 | 404.7272 | 10 | 3.788 | 2 | 10 | 240 | 2R x 3.5C x 240 sq.mm Al XLPE armd | 505.2786 | 0.2427% | OK | Ampacity
I02 | DG set | Main LT Panel (via AMF) | DG rating | 320 | 445.1857 | 500 | 25 | 2 | 0.87 | 0.71 | 0.6177 | 404.7272 | 10 | 2.2373 | 3 | 10 | 240 | 2R x 3.5C x 240 sq.mm Al XLPE armd | 505.2786 | 0.411% | OK | Ampacity
F01 | Main LT Panel | GF Floor DB | Load_Schedule MD | 21.3512 | 29.7039 | 32 | 20 | 1 | 0.87 | 0.71 | 0.6177 | 51.8051 | 1 | 20.9569 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.6075% | OK | Ampacity
F02 | Main LT Panel | FF Floor DB | Load_Schedule MD | 10.702 | 14.8887 | 16 | 30 | 1 | 0.87 | 0.71 | 0.6177 | 25.9025 | 1 | 27.8735 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.4568% | OK | Ampacity
F03 | Main LT Panel | SF Floor DB | Load_Schedule MD | 10.702 | 14.8887 | 16 | 40 | 1 | 0.87 | 0.71 | 0.6177 | 25.9025 | 1 | 20.9051 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.609% | OK | Ampacity
F04 | Main LT Panel | HVAC Panel (terrace) | Load_Schedule MD | 93.4706 | 130.0368 | 160 | 45 | 1 | 0.87 | 0.71 | 0.6177 | 259.0254 | 7 | 2.1276 | 3 | 7 | 120 | 1R x 3.5C x 120 sq.mm Al XLPE armd | 162.4551 | 0.8137% | OK | Ampacity
F05 | Main LT Panel | Lift Panel | Load_Schedule MD | 12.9412 | 18.0038 | 20 | 50 | 1 | 0.87 | 0.71 | 0.6177 | 32.3782 | 1 | 13.8304 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.9206% | OK | Ampacity
F06 | Main LT Panel | Pump & STP Panel | Load_Schedule MD | 9.5294 | 13.2574 | 16 | 30 | 1 | 0.87 | 0.71 | 0.6177 | 25.9025 | 1 | 31.3033 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.4067% | OK | Ampacity
F07 | Main LT Panel | Fire Pump Panel | Full load (fire pump + jockey) | 39.6471 | 55.1572 | 63 | 25 | 1 | 0.87 | 0.71 | 0.6177 | 101.9913 | 3 | 9.0287 | 1 | 3 | 35 | 1R x 3.5C x 35 sq.mm Al XLPE armd | 74.124 | 0.6421% | OK | Ampacity
F08 | Main LT Panel | UPS input | UPS input demand | 33.6163 | 46.7672 | 50 | 15 | 1 | 0.87 | 0.71 | 0.6177 | 80.9454 | 2 | 17.7475 | 1 | 2 | 25 | 1R x 3.5C x 25 sq.mm Al XLPE armd | 59.9169 | 0.4511% | OK | Ampacity
F09 | Main LT Panel | EV Charger DB | Load_Schedule MD | 14.9495 | 20.7978 | 25 | 40 | 1 | 0.87 | 0.71 | 0.6177 | 40.4727 | 1 | 14.9655 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.8507% | OK | Ampacity
F10 | Main LT Panel | External Lighting DB | Load_Schedule MD | 4.4444 | 6.1831 | 16 | 60 | 1 | 0.87 | 0.71 | 0.6177 | 25.9025 | 1 | 33.559 | 1 | 1 | 16 | 1R x 4C x 16 sq.mm Al XLPE armd | 47.5629 | 0.3794% | OK | Ampacity
F11 | Main LT Panel | APFC Panel | 1.43 x capacitor kVA (IEC 60831) | 107.25 | 149.2068 | 160 | 10 | 1 | 0.87 | 0.71 | 0.6177 | 259.0254 | 7 | 8.3441 | 1 | 7 | 120 | 1R x 3.5C x 120 sq.mm Al XLPE armd | 162.4551 | 0.2075% | OK | Ampacity
Fire-pump feeder sized on full load (not demand) and must be routed separately as a fire-survival circuit (NBC 2016 Part 4). Short-circuit withstand S ≥ I·√t / k (k = 94, Al XLPE) to be checked against breaker let-through energy.

## Earthing
Earthing design per IS 3043:2018
A. Single pipe electrode
Item | Value | Unit | Formula
Resistance of one electrode, R1 | 12.6992 | Ω | R = ρ / (2πL) x ln(4L / d)
Mutual factor α | 0.10444 | - | α = ρ / (2π R1 s)
B. Interconnecting strip electrode
Item | Value | Unit | Formula
Resistance of buried strip, Rs | 1.6672 | Ω | R = ρ / (2πL) x ln(2L² / (w t))
C. Number of electrodes (in line) + strip in parallel
|  |  |  | n | λ | Rn (Ω) | Grid R (Ω) | Meets target?
Electrodes required in main grid | 7 | nos | Smallest n with grid R ≤ target. Rn = R1(1 + λα)/n; grid = Rn ∥ Rs (mutual coupling ignored, so measure after installation) | 1 | 0 | 12.6992 | 1.4738 | No
Grid resistance achieved | 0.98565 | Ω |  | 2 | 1 | 7.0128 | 1.347 | No
|  |  |  | 3 | 1.66 | 4.967 | 1.2482 | No
|  |  |  | 4 | 2.15 | 3.8877 | 1.1668 | No
|  |  |  | 5 | 2.54 | 3.2136 | 1.0977 | No
|  |  |  | 6 | 2.87 | 2.7509 | 1.0381 | No
|  |  |  | 7 | 3.15 | 2.411 | 0.98565 | Yes
|  |  |  | 8 | 3.39 | 2.1494 | 0.93894 | Yes
|  |  |  | 9 | 3.61 | 1.943 | 0.8973 | Yes
|  |  |  | 10 | 3.81 | 1.7752 | 0.85977 | Yes
D. Earthing conductor sizing (adiabatic)
Item | Value | Unit | Formula
Prospective earth fault current | 9738.4383 | A | Taken = LV 3-ph fault level (conservative)
Minimum area, S | 121.7305 | mm² | S = I √t / k
With corrosion allowance | 182.5957 | mm²
Selected GI strip (main earth conductor) | 32 x 6 | mm
E. Dedicated earth pits (in addition to main grid)
Purpose | Nos |  | Note
Transformer neutral | 2 |  | Bonded to grid at one point (TN-S)
DG neutral | 2
UPS / IT clean earth | 2 |  | Isolated electronic earth, ≤ 0.5 Ω
Lightning protection | 2 |  | IS/IEC 62305 down-conductor pits

## Ref_Tables
Reference tables
Source: Havells International Cables catalogue, 0.6/1 kV Al XLPE armoured, Tables 16 (3.5C, 25-300) & 20 (4C, 16). Ampacity in air at 30°C. | [5 empty] | UF (refl. 70/50/20) | [6 empty] | IS 3043 parallel-electrode factor
Size (mm²) | Ampacity in air 30°C (A) | Max R @20°C (Ω/km) | X (Ω/km) | mV/A/m (3-ph, R @90°C) | SC rating 1 s (kA) | Room index K | UF | Breaker In (A) | Transformer (kVA) | DG set (kVA) | UPS (kVA) | Battery (Ah) | n | λ (in line) | GI strip | Area (mm²)
16 | 77 | 1.91 | 0.083 | 4.2439 | 1.5 | 0.6 | 0.45 | 16 | 100 | 15 | 6 | 7 | 1 | 0 | 25 x 3 | 75
25 | 97 | 1.2 | 0.082 | 2.6686 | 2.35 | 0.8 | 0.53 | 20 | 160 | 20 | 10 | 9 | 2 | 1 | 25 x 6 | 150
35 | 120 | 0.868 | 0.08 | 1.9325 | 3.29 | 1 | 0.58 | 25 | 200 | 25 | 15 | 12 | 3 | 1.66 | 32 x 6 | 192
50 | 146 | 0.641 | 0.079 | 1.43 | 4.7 | 1.25 | 0.63 | 32 | 250 | 30 | 20 | 18 | 4 | 2.15 | 40 x 6 | 240
70 | 187 | 0.443 | 0.077 | 0.99275 | 6.58 | 1.5 | 0.67 | 40 | 315 | 40 | 30 | 26 | 5 | 2.54 | 50 x 6 | 300
95 | 227 | 0.32 | 0.077 | 0.72302 | 8.93 | 2 | 0.72 | 50 | 400 | 62.5 | 40 | 42 | 6 | 2.87 | 50 x 10 | 500
120 | 263 | 0.253 | 0.076 | 0.57704 | 11.28 | 2.5 | 0.75 | 63 | 500 | 82.5 | 60 | 65 | 7 | 3.15 | 75 x 10 | 750
150 | 304 | 0.206 | 0.076 | 0.47602 | 14.1 | 3 | 0.78 | 80 | 630 | 100 | 80 | 100 | 8 | 3.39
185 | 347 | 0.164 | 0.076 | 0.38725 | 17.39 | 4 | 0.81 | 100 | 800 | 125 | 100 | 120 | 9 | 3.61
240 | 409 | 0.125 | 0.075 | 0.30648 | 22.56 | 5 | 0.83 | 125 | 1000 | 160 | 120 | 150 | 10 | 3.81
300 | 471 | 0.1 | 0.075 | 0.25727 | 28.2 |  |  | 160 | 1250 | 200 | 160 | 200
R from catalogue (20°C DC) corrected to 90°C with α(Al) = 0.00403/°C. Catalogue gives no reactance, so X is a typical value for multicore XLPE. 16 mm² taken from the 4-core table (smallest 3.5C size is 25 mm²). | [7 empty] | 200 | 1600 | 250 | 200
[8 empty] | 250 | 2000 | 320
[8 empty] | 320 |  | 380
[8 empty] | 400 |  | 500
[8 empty] | 500 |  | 625
[8 empty] | 630 |  | 750
[8 empty] | 800 |  | 1010
1000
1250
1600
2000
2500